- Check current firmware version

- Before starting any update/upgrade actions check which firmware version is currently in the device.

- The current firmware version can be checked by using the ETS-function Device Info:

- (Device shall be connected with mains and KNX before the device info is read via the USB-interface.)

- Firmware version:0.1.0

- Requirements for a firmware update – Formatting the SD card

This application note describes the procedure for updating a device to a new firmware version.

The KNX-DALI-Gateways Basic (MTN6725-0003 and MTN6725-0004) are designed to perform firmware updates easily.  The update is performed via a micro SD card and the corrresponding SD card slot on the device. Any new developments or improvements that may be required can be easily loaded onto the device via updates.

A firmware update can only be performed via a flash memory card of the type microSD (measurements: 11 x 15 mm). Please purchase the correct card with at least 1GB memory from a computer or photo shop.

An update is only possible if the micro SD card has the

FAT32 format. Most cards sold today with 2-32 GB are

already FAT32-formatted by default.!

It is therefore necessary to change the  format of the card to

FAT32 first.

Simply use a Windows File –Explorer to change the format.

Click with the right mouse button on the micro SD card and

select the format. Please see next screen shot below.

If the file-explorer does not offer this opportunitiy search for a formatting tool as freeware for example.

Screenshot using File Explorer (right mouse button) for format check and change:

- Update procedure

To update the firmware version, please first unzip the zip archive that is available with this application note. The zip-file contains this description (pdf-file) together with the firmware upgrade with the extension *.bin. The zip-files have name according the following example: Update_V0.1.3_MTN6725-0003.zip

Please copy the corresponding bin-file directly into the root directory of the SD card. There should be only one bin-file in the root directory.

Firmware bin file		Article number

D1_00C.bin		MEG6725-0003

D1_064.bin		MTN6725-0003

D2_00C.bin		MEG6725-0004

D2_064.bin		MTN6725-0004

Be careful: The firmware *.bin-files have always the same name, without an indicating version.

Attention: Please remember to follow all safety regulations when working on an already installed gateway.

- The gateway, the connected ECGs and any other devices in the system need to be disconnected from the power supply before any work is carried out!

For update purposes, the KNX DALI Gateways mentioned above are equipped with a SD card slot in the top right-hand corner.  On delivery the opening of the slot is covered with an adhesive label.To  insert a card, please carefully remove the label.

After the label has been removed, carefully insert the micro SD card into the disconnected gateway in such a way that the row of contacts points downwards and the recess in the card points towards the left. Please make sure to insert the card straight into the slot  without any angle or bend. You will notice a slight pressure when the contact row has snapped into place.

After the card has been inserted, re-connect first the KNX line. Then connect  the mains power supply whilst simultanously keeping the KNX-programming button pressed down. After a few seconds, the KNX-programming LED starts flashing. Now you can release  the KNX-programming button and the update process will start. The process takes only a few seconds. At the end the Man-LED briefly lights up once.  (If not check micro SD card, FAT 32, *.bin file in root directory)

Important: After the update, disconnect the gateway and the lamps from the power supply and remove the micro SD card. Please remember to cover the card slot with the previously removed adhesive label before re-connecting the power! This helps also to prevent dust on the contacts.

- After the update the device is directly ready to use, so no ETS download is needed again if configuration was already  downloaded before the update.

Abbreviations:

ECG	Electronic Control Gear, the DALI electronic of a lamp, also called ballast,

HSV	Hue (=colour), Saturation, Value (=brightness)

RGB	Red, Green, Blue,

RGBW	Red, Green, Blue, White

- Revision tracking

Firmware version 0.1.0   released 15 October 2017 	delivered with pilot series

Firmware version 0.1.1   released  21 February  2018	Firmware version: 0.1.1

Problems solved:

- RGB, HSV and RGBW control via Broadcast does not work for Blue=100% (DALI 254 not 255!)  corrected

- Saving scenes via an object with MSB set does not work  corrected

- After a power cut, the operating hours are not correctly exported from memory -> corrected

- The plug-in display “operating hours“ shows seconds  corrected and changed to hours

--------------------------------------------------------------------------------------------------------------------------------------------------

Firmware Version 0.1.2   released  06 April 2018	Firmware Version: 0.1.2

Problems solved:

- If a RGB colour is loaded via scenes and the colour subsequently set via value (single objects) or dimming, an incorrect colour is displayed  corrected

- If the colour values of several groups are dimmed simultanously via a central object, only the last group reacts  corrected

- If the colour values of several groups are dimmed simultanously via  different objects, only the last group reacts  corrected

- A running dim process “colour dimming“ does not stop when a  scene is recalled  corrected

Firmware Version 0.1.3   released  18 May 2018	Firmware Version: 0.1.3

Problems solved:

- If a HSVW colour is programmed via ETS in a Scene the adjusted colour is not correct  corrected

- If RGBW colour is adjusted by a Scene the status object is not correct (Byte position mismatch)  corrected

- If RGBW colour is adjusted via Broadcast 6 Byte Object in status 6Byte Object the Bits for validity are not correct (Bit position mismatch)  corrected

Firmware Version 0.1.4 released 03. September 2018 Firmware Version: 0.1.4

So devices produced after this date will have the new version running, no manual update needed.

Bugs fixed:

On color control via broadcast-object RGBW / HSVW device is not reacting on white telegramm, if white is sent

first -> corrected,

Parameter setting „Cycle time for DALI failure request = 0,5 sec.“ is not working corrected,

RGBW control via time control (Templates) works only partially corrected,

Only in 2 channel device: Saving scenes via an object with MSB set does not work corrected.

Optimized:

Some DALI-2 Osram ECGs generate short interruptions on the DALI Bus. Due to this there can appear problems

in new installation process optimized and adapted to DALI-2 standard,

TPUART driver may loose very rarely telegramms or send busy telegrams optimized,

Max. APDU-Length modified from 15 to 55 download can be faster optimized,

If ECG mains power is switched OFF with an external switch actuator and scenes are activated sometimes scene is not started correctly optimized, scenes activate ECG power before sending DALI telegram,

If ECG mains power is switched OFF with an external switch actuator and the device is controlled by time control templates ECG power is not switched on optimized, time control templates activate ECG power before sending DALI telegram.